SECTION 26 51 13

INTERIOR LIGHTING FIXTURES, LAMPS, AND BALLASTS

Equipment Specified in this section:

GLD-LV-LED-L-1X50W

GLD-LV-LED-S-1X50W

GLD-LV-LED-L-1X100W

GLD-LV-LED-S-1X100W

GLD-DALI-LED-L-1X50W

GLD-DALI-LED-S-1X50W

GLD-DALI-LED-L-1X100W

GLD-DALI-LED-S-1X100W

GLD-DALI-LED-L-2X50W

GLD-DALI-LED-S-2X50W

Table of Contents

SECTION 26 51 13	1

INTERIOR LIGHTING FIXTURES, LAMPS, AND BALLASTS	1

SECTION 26 51 13	3

INTERIOR LIGHTING FIXTURES, LAMPS, AND BALLASTS	3

PART 1	GENERAL	3

1.1	SUMMARY	3

1.2	REFERENCES	3

1.3	DEFINITIONS	4

1.4	ACTION SUBMITTALS	4

1.5	CLOSEOUT SUBMITTALS	4

1.6	QUALITY ASSURANCE	4

1.7	COORDINATION	5

1.8	PROJECT CONDITIONS	5

PART 2	PRODUCTS	5

2.1	MANUFACTURERS	5

2.2	LED DRIVER TYPE 1	5

2.3	LED DRIVER TYPE 2	6

2.4	LED DRIVER TYPE 3	8

2.5	LED DRIVER TYPE 4	9

2.6	LED DRIVER TYPE 5	10

2.7	LED DRIVER TYPE 6	12

PART 3	EXECUTION	13

3.1	EXAMINATION	13

3.2	PREINSTALLATION MEETING	13

3.3	INSTALLATION	13

3.4	SYSTEM STARTUP	14

3.5	ADJUSTING	14

3.6	DEMONSTRATION	14

3.7	FIELD QUALITY CONTROL	14

3.8	CLOSEOUT ACTIVITIES	14

SECTION 26 51 13

INTERIOR LIGHTING FIXTURES, LAMPS, AND BALLASTS

Specifier: The Specifier/Design Professional is responsible for the accuracy of all project specifications, including system application and coordination with related sections.  This guide specification is provided as a convenience and requires editing to match actual project requirements.  CRESTRON ELECTRONICS, INC. SHALL NOT BE LIABLE FOR ANY DAMAGES ARISING OUT OF THE USE OF ANY OF ITS GUIDE SPECIFICATIONS.  For Crestron design assistance and design review please contact Sales Support Services Department at   800.237.2041 or techsales@crestron.com.

GENERAL

SUMMARY

Section Includes:

Dimmable LED drivers:

0-10V Control

Dimmable LED drivers:

DALI Control

Related Information:

Section 12 24 13 Roller Window Shades

Section 25 08 00 Commissioning of Integrated Automation

Section 25 10 00 Integrated Automation Network Equipment

Section 25 11 13 Integrated Automation Network Servers

Section 25 13 13 Integrated Automation Control and Monitoring Network Supervisory Control

Section 25 13 19 Integrated Automation Control and Monitoring Network Interoperability

Section 25 15 16 Integrated Automation Software for Control and Monitoring Networks

Section 26 05 00 Common Work Results For Electrical

Section 26 27 26 Wiring Devices

Section 26 51 00 Interior Lighting

Section 27 15 00 Communications Horizontal Cabling

Section 27 41 00 Audio-Video Systems

REFERENCES

Underwriters Laboratories, Inc. (UL):

UL1310 and 8750, Class 2 output

Federal Communications Commission (FCC):

FCC Title 47 Telecommunications CFR Part 15 Class B

DEFINITIONS

Daylight Harvesting:  The dimming of electric lighting sources when natural daylight is available.

DALI:  Digital addressable lighting interface.

Load Shedding:  Intentional reduction of power consumption to avoid total power disruption due to overloading the circuits or reduction of power consumption to avoid crossing an agreed on threshold of power usage.  Load shedding lighting ballasts reduce the light level in response to a signal on the power line.

Monitor:  Acquisition and presentation of status or operating condition of microprocessors or electrical devices in the network of the monitoring device or program.

Scene:  Predetermined position of shades and light levels.

Scene Selection:  Grouping of lighting and window shade controls into groups that will respond to a single scene command.

Transmission Control Protocol/Internet Protocol (TCP/IP):  Networking protocols for exchanging data over the World Wide Web and Local Area Networks.

MTBF: Mean time between failures.

ACTION SUBMITTALS

Product Data: For each type of product required for complete electronic dimmable ballast system, demonstrating compliance with requirements.

Shop Drawings: Indicate the following:

Schematic diagram showing complete LED unit with dimmable driver system and integrated control equipment and accessories.

Describe Circuits and emergency circuits with capacity and phase, control zones, load type and voltage per circuit.

CLOSEOUT SUBMITTALS

Operating and maintenance instructions.

Record drawings of electronic dimmable ballast system.

Provide copy of warranty.

QUALITY ASSURANCE

Manufacturer Qualification:  Manufacturer of LED lighting components with minimum 10 years record of satisfactory manufacturing and support of lighting and control components.

Source Requirements:  Provide LED drivers [and DALI-compliant drivers] through a single source from same manufacturer as lighting control equipment.

COORDINATION

Coordinate dimmable LED driver outfitted luminaire system with systems and components specified in the following sections:

Division 26 Section “Network Lighting Controls”.

Division 11 Section "Audio-Visual Equipment".

Division 12 Section "Window Treatments".

Division 23 Section "Instrumentation and Control for HVAC".

Division 25 Section "Integrated Automation Control of Electrical Systems".

Division 26 Section “Network Lighting Controls”.

Division 26 Section "Panelboards".

Division 26 Section "Wiring Devices".

Division 26 Section "Lighting Devices".

Division 26 Section "Interior Lighting".

Division 27 Section "Communications Horizontal Cabling".

Division 28 Section "Electronic Access Control and Intrusion Detection".

PROJECT CONDITIONS

Environmental Conditions Range:

Temperature: 32 to 104 degrees F (0 to 40 degrees C).

Relative Humidity:  10 – 90 percent, noncondensing.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  Subject to compliance with requirements, provide products of Crestron Electronics, Inc., Rockleigh, NJ 07647,  Phone (800)237-2041, Fax: (201)767-1903, www.crestron.com with the following components and characteristics.

LED DRIVER TYPE 1

Single channel dimming driver:

Basis of design Product:

Crestron GLD-LV-LED-L-1X50W (long case)

Crestron GLD-LV-LED-S-1X50W (short case)

Control interface: 0-10V

Driver shall communicate with control processor through a 0-10V control interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 0.7 Amp Maximum

Output:

Dimmed LED channels: 1

Dimmed LED groups: 2

Power: 50W

Maximum Voltage: 55V

Compatible LED controllers: current sink and current source

Current Range: 200mA to 1,050mA per output

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.18” (30mm); W: 17.48” (444mm); D: 8.83” (21mm)

Short Case: H: 2.99” (76mm); W: 5.12” (130mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

LED DRIVER TYPE 2

Single channel dimming driver:

Basis of design Product:

Crestron GLD-LV-LED-L-1X100W (long case)

Crestron GLD-LV-LED-S-1X100W (short case)

Control interface: 0-10V

Driver shall communicate with control processor through a 0-10V control interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 1.5 Amp Maximum @ 120VAC/60Hz; 0.5 Amp Maximum @ 230VAC/50Hz; 0.45 Amp Maximum @277 60Hz

Output:

Dimmed LED channels: 1

Dimmed LED groups: 4

Power: 100W

Maximum Voltage: 60V

Compatible LED controllers: current sink and current source

Current Range: 200mA to 1,050mA per output

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.61” (41mm); W: 14.57” (370mm); D: 1.18” (30mm)

Short Case: H: 3.15” (80m); W: 9.06” (230mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

0-10V Control

Driver shall communicate with control processor through a 0-10V control interface by same manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

LED DRIVER TYPE 3

Single channel dimming driver:

Basis of design Product:

Crestron GLD-DALI-LED-L-1X50W (long case)

Crestron GLD-DALI-LED-S-1X50W (short case)

Control interface: DALI

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 7.7 Amp

Output:

Dimmed LED channels: 1

Dimmed LED groups: 2

Power: 50W

Maximum Voltage: 55V

Compatible LED controllers: current sink and current source

Current Range: 200mA to 1,050mA per output

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.18” (30mm); W: 17.48” (444mm); D: 8.83” (21mm)

Short Case: H: 2.99” (76mm); W: 5.12” (130mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

LED DRIVER TYPE 4

Single channel dimming driver:

Basis of design Product:

Crestron GLD-DALI-LED-L-1X100W (long case)

Crestron GLD-DALI-LED-S-1X100W (short case)

Control interface: DALI

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 1.5 Amp Maximum @ 120VAC/60Hz; 0.5 Amp Maximum @ 230VAC/50Hz; 0.45 Amp Maximum @277 60Hz

Output:

Dimmed LED channels: 1

Dimmed LED groups: 4

Power: 100W

Maximum Voltage: 60V

Compatible LED controllers: current sink and current source

Current: 1.5 Amp Maximum @ 120VAC/60Hz; 0.5 Amp Maximum @ 230VAC/50Hz; 0.45 Amp Maximum @277 60Hz

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.61” (41mm); W: 14.57” (370mm); D: 1.18” (30mm)

Short Case: H: 3.15” (80m); W: 9.06” (230mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

DALI Control

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

LED DRIVER TYPE 5

Single channel dimming driver:

Basis of design Product:

Crestron GLD-DALI-LED-L-2X50W (long case)

Crestron GLD-DALI-LED-S-2X50W (short case)

Control interface: DALI

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 7.7 Amp

Output:

Dimmed LED channels: 2

Dimmed LED groups: 1 per channel

Power: 50W

Maximum Voltage: 55V

Compatible LED controllers: current sink and current source

Current Range: 200mA to 1,050mA per output

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.18” (30mm); W: 17.48” (444mm); D: 8.83” (21mm)

Short Case: H: 2.99” (76mm); W: 5.12” (130mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

DALI Control

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

LED DRIVER TYPE 6

Single channel dimming driver:

Basis of design Product:

Crestron GLD-DALI-LED-L-2X100W (long case)

Crestron GLD-DALI-LED-S-2X100W (short case)

Control interface: DALI

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Input:

Line Voltage: 120-277VAC

Frequency: 50/60Hz

Current: 1.5 Amp Maximum @ 120VAC/60Hz; 0.5 Amp Maximum @ 230VAC/50Hz; 0.45 Amp Maximum @277 60Hz

Output:

Dimmed LED channels: 2

Dimmed LED groups: 2 per channel

Power: 100W

Maximum Voltage: 60V

Compatible LED controllers: current sink and current source

Current: 1.5 Amp Maximum @ 120VAC/60Hz; 0.5 Amp Maximum @ 230VAC/50Hz; 0.45 Amp Maximum @277 60Hz

Dimming:

Range: 100% to 0%

Curve: linear or Logarithmic

Driver shall include an interface for programming configurable parameters including:

Output current (per LED group)

Dimming curve

Minimum dimming level

NTC Temperature

Dimensions:

Long Case: H: 1.61” (41mm); W: 14.57” (370mm); D: 1.18” (30mm)

Short Case: H: 3.15” (80m); W: 9.06” (230mm); D: 1.18” (30mm)

General:

Driver housing shall be constructed of painted metal with no sharp edges.

Wiring termination: push button terminal block.

Drivers shall be configured and installed in fixture by the fixture manufacturer.

DALI Control

Driver shall communicate with DALI compatible devices.

Driver shall support standard DALI protocol.

Driver shall communicate with control processor through DALI to IP control network interface by same manufacturer.

Environmental Rating: -40 to 122 degrees F (-40 to 50 degrees C).

MTBF: 480,000 hours

Driver Certifications:

CE; UL: Recognized Component for US and Canada according to UL1310 and UL8750; US: Class 2 output; Canada: Non-Class 2 output; IEC 61347-1, IEC 61347-2-13, IEC 62384 + A1, EN 55015 + A1, EN 55022 + A1, IEC 61000-3-2, IE 61547 + A1, IEC 62386-101/102/207; FCC: Title 47CFR Part 15 Class B

EXECUTION

EXAMINATION

Prior to installation, examine work area to verify measurements, and that commencing installation complies with manufacturer's requirements.

PREINSTALLATION MEETING

Installer of Electronic Ballast Lighting System to coordinate a meeting of the mechanical and electrical engineer, mechanical and electrical contractor, lighting, window shade and HVAC equipment manufacturers.  Include any designers and contractors for any other direct digital control system designed to interact with product of this Section.

Discuss interconnection and interoperability of other equipment with Electronic Ballast Lighting System.

INSTALLATION

Comply with requirements of Division 26 Sections "Common Work Results for Electrical."

Install Electronic Ballast in accordance with manufacturer's instructions.

Grounding:  Provide electrical grounding in accordance with NFPA 70.

SYSTEM STARTUP

Provide manufacturer's system startup and adjustment.

Switch each load on and off.  Test dimming features. Test system integration to the satisfaction of engineer.  Provide a written report of test and outcomes.

Perform operational testing to verify compliance with Specifications.  Adjust as required.

ADJUSTING

Within 12 months of the date of Substantial Completion provide onsite service to adjust the system to account for actual occupied conditions.

DEMONSTRATION

Factory authorized service representative to instruct owner's staff to adjust, operate and maintain electronic dimmable ballast systems; and provide instruction using the system software.

FIELD QUALITY CONTROL

Manufacturer's Field Services:  Qualified manufacturer's field representative to perform on-site system inspection, startup, and owner demonstration and training.

Participation in Preinstallation Conference and pre-wire inspection.

Owner programming conference.

Owner demonstration and training.

CLOSEOUT ACTIVITIES

Demonstration:  Schedule demonstration with Owner.

Training:

Furnish set of approved submittals and record drawings of actual installation for Owner's personnel in attendance at training session.

# END OF SECTION 26 51 13